# Operational Assurance Prescribed Electrical Work Compliance Procedure COMPO801

June 2024

Contents

1.0	Change Management	3

2.0	Purpose	3

3.0	Scope	3

4.0	Definitions	4

5.0	General Legislative Requirements	4

6.0	Responsibilities	6

7.0	Process Map	7

8.0	Notification Requirements for HT Infrastructure	8

9.0	Inspection and Auditing Requirements for HT Infrastructure	8

10.0	CEC Distribution and Storage Requirements	8

11.0	ESMS Record of Electrical Work Distribution and Storage Requirements	9

12.0	Practitioners Registers	9

13.0	Associated Documents	10

| Hydro Tasmania document control |  |  |  |
| --- | --- | --- | --- |
| Title | Operational Assurance Prescribed Electrical Work Compliance Procedure |  | Version:2 |
|  |  | Document owner: | Ashlee Geard |
|  |  | Date created: | 18th March 2024 |
| Approver: | Head of AMO | Date approved: | 1st May 2024 |
|  |  | Date effective: | 1st June 2024 |

# Change Management

New document developed and supersedes “Technical and Operations Standard – Certificate of Electrical Compliance Procedure”; and

New nomenclature.

# Purpose

The purpose of this procedure is to:

Define how prescribed electrical work is managed, and

Ensure compliance to relevant Legislation and Codes of Practice.

# Scope

This procedure applies to:

All prescribed Electrical work on Hydro Tasmania’s installations and infrastructure;

Hydro Tasmania performing Prescribed Electrical Work for a customer as an Electrical Contractor; and

Hydro Tasmania performing unpaid Prescribed Electrical Work on a Customers installation.

- This procedure identifies four options to resource the management and control of Prescribed Electrical Work

An authorised resource working under the A&I Electrical Safety Management Scheme;

An external Electrical Contractor;

An Electrical Practitioner employed by Hydro Tasmania; or

The nominated manager under Hydro Tasmania’s Electrical Contractor’s Licence.

- For these four options, this procedure identifies who is responsible for recording, certifying, notifying and inspecting the work.

# Definitions

As documented in the Definition of Standard Terms procedure.

Operational Assurance Definition of Standard Terms COMP0002.docx

# General Legislative Requirements

The Occupational Licensing Act (OLA), Occupational Licensing Regulations (OLR) and the associated Codes of Practice apply to any Prescribed Electrical Work performed on electrical Infrastructure or electrical installations.

Prescribed electrical work can only be performed by:

- A licenced practitioner;

- Someone in training under the supervision of a licenced practitioner; or

- Someone working under an approved Electrical Safety Management Scheme (ESMS).

Note: Working under an approved ESMS gives an exemption to any requirement specified in the OLA or OLR.

The electrical practitioner performing the prescribed electrical work must certify that their work complies and has been tested, to the relevant standards expected for that work.

A record of all prescribed electrical work must be kept for a minimum of 10 years. The Certificate of Electrical Compliance (CEC) meets the minimum requirements for recording, certification and notification identified in the OLR. The Assets and Infrastructure Electrical Safety Management Scheme Record of Electrical Work meets the requirements for recording, certification and notification identified in the A&I ESMS.

Note: While the record of electrical work can take many forms, HT requires, as a minimum, that one of these two forms is completed for all installation and infrastructure electrical work.

An electrical contractor’s licence is required when conducting the business of an electrical contractor.

Note: This would apply where HT is managing and controlling work on an installation or infrastructure that it does not own and is paid for the work. HT is not required to hold an electrical contractor’s licence when managing and controlling work on its own infrastructure or installations or performing unpaid work. Payment of a connection or service fee is not considered to be payment for the work. Under the Standards of Electrical Work Code of practice 2013, where prescribed electrical work is performed and there is no requirement to hold an electrical contractor licence it is assumed that the contractor and nominated manger obligations for the transfer to the person in management and control of the work.

Notification is required to TechSafe for the following:

- Any substantial upgrade or modification to an installation (within 3 days after it is energised or capable of being energised);

- Private HV installation (3 days prior to commencement of work and approval required prior to energisation); and

- Hazardous area installation (3 days prior to commencement of work and approval required prior to energisation).

Note:

- HT is not required to externally notify work on its own infrastructure; however, it should have controls in place to ensure any work on its infrastructure complies with minimum standards and is safe;

- Any holder of an electrical licence, who is aware of any defective or dangerous electrical infrastructure or installation, has a duty correct and/or notify the situation.

- The owner/occupier has the obligation to ensure any prescribed electrical work on their premises is performed by an appropriately licenced person; and

- As well as meeting any Licensing requirements there is a WHS Act requirement to ensure anyone performing work is competent.

# Responsibilities

| Work Requestor | Work Planner | Work Authoriser | Work Supervisor | Specialist Worker Roles | Workers | Advice/Support |
| --- | --- | --- | --- | --- | --- | --- |
| - Legislation (Applies to any Prescribed Electrical Work performed on existing or new installations and infrastructure) | Planner/Scheduler - Works Co-ordinator - Planner - Project/Job Manager | Owner/Occupier - Production Manger - Building Services Officer - Project/Job Manager - Customer | Person managing and controlling the work - HT Licenced Practitioner - HT Nominated Manager - Electrical Contractor - ESMS Resource | Person to maintain the practitioner register - Operational Assurance Manager - HT Nominated Manager - Electrical Contractor | Person performing the work - Licenced Practitioner - Apprentice - ESMS Resource - REWL | Persons with knowledge of the relevant legislation and this procedure - Operational Assurance team |
|  |  |  |  | Inspection of Electrical Installations - TechSafe |  |  |
|  |  |  |  | Inspection and auditing of Electrical Infrastructure - Operational Competency Manager |  |  |
|  |  |  |  | Access to private property/premises to perform work associated with HT’s infrastructure - Electricity Officers |  |  |

# Process Map

# Notification Requirements for HT Infrastructure

The following work must be notified to the Operational Competency Manager, by email to operational.compliance@hydro.com.au :

All additions and substantial modifications to Hydro Tasmania’s high voltage infrastructure, prior to:

- Commencing work; and

- Energisation.

All hazardous area electrical work on Hydro Tasmania’s infrastructure, prior to:

- Commencing work; and

- Energisation.

All other additions and substantial modifications to Hydro Tasmania’s infrastructure, within 3 days of:

- Being energised; or

- Being capable of being energised.

# Inspection and Auditing Requirements for HT Infrastructure

Inspections and audits will be incorporated into Asset Management and Investment annual audit schedule to ensure:

- Compliance to this procedure; and

- Standards of electrical work are maintained.

One off inspections may be carried out, at the discretion of the Operational Competency Manager if there is significant or unusual risk presented by the work.

# CEC Distribution and Storage Requirements

All copies need to be kept and available on request for 10 years from when the work was completed.

- Green copy stays in its booklet. This is the practitioner’s record of the work they performed.

- Blue copy is sent to TechSafe for notifiable work on installations. If the work is not notifiable to TechSafe the copy stays in its booklet.

- White copy is given to the owner/occupier (customer) for the work.

- Where the work is on a Hydro Tasmania installation or infrastructure:

- The white copy will be stored in the Compliance Folder by the owner/occupier (customer), at the site where the work was completed; and

- A scanned copy sent the Operation Assurance Team where they will store the file against the site where the work was completed

- Where the work has been performed under Hydro Tasmania’s Contractor’s Licence a scanned copy will be sent to the Nominated Manager. This is the Nominated Manager’s record of the work performed under the Contractor’s Licence.

# ESMS Record of Electrical Work Distribution and Storage Requirements

All copies shall be kept and available on request for 10 years from when the work was completed.

- The original is kept by the person performing the work. This is the ESMS Authorised Resource’s record of the work they have performed;

- A scanned copy will be stored in the Compliance Folder by the owner/occupier (customer), at the site where the work was completed; and

- A scanned copy is sent to the Operation Assurance Team where they will store the file against the site where the work was completed

# Practitioners Registers

Where work is performed under Hydro Tasmania’s Electrical Contractors Licence, the Nominated Manager is responsible to maintain the practitioner’s register.

Where work is performed for Hydro Tasmania by an Electrical Contractor, the Electrical Contractor or their Nominated Manager is responsible to maintain the practitioner’s register.

Where work is performed and does not require a Contractor’s Licence the Operational Assurance Team is responsible to maintain the practitioner’s register.

# Associated Documents

Regulatory documents:

Occupational Licensing Act

Occupational Licensing Regulations

Occupational Licensing (Standards of Electrical Work) Code of Practice

Occupational Licensing (private high voltage electrical work- Certification and Energisation) notice

Occupational Licensing (Fit and proper) Code of Practice

Occupational Licensing (Approved Forms - Electrical) Notification

Managing Electrical Risks in the Workplace - Code of Practice

Certificate of Electrical Compliance Form

Occupational Licensing (supervision of prescribed work) code of practice

Hydro documents:

Electrical Safety Management Scheme 2016

Assets and Infrastructure Electrical Safety Management Scheme Record of Electrical Work

Electrical practitioners and Linesman competence matrix (Practitioners Register)

External documents:

RBD Electrical Works Notification Requirements checklist.pdf