## Slide 1: Integrated Hazard & Operability Study
Preparation Guide

## Slide 2
Contents
Contents are hyperlinked to slides for quick access
Note: Each slide has a Contents slide link to return to this slide
Planning and Preparation
    Study Type
    Study Tier
    Define the Scope
    Prepare Study Materials
    Engage the Facilitator & Scribe
    Select a Suitable Location
    Schedule & Invite Participants
    Common Pitfalls & How to Avoid Them
On the day Presentation Template
    Welcome & introductions
    Scope & objectives
    Hazard and Opportunity Identification & Analysis
    Study Finalisation Review Prompts
    General
    Pre-Commissioning & Commissioning
    Handover / Return to Service
    Recommendations & Actions
    Next actions
This is a practical guide to support the planning and facilitation of hazard studies, promoting consistency and quality.
2. Prompt Libraries and Failure Cause Lists
    Hazard Identification (HAZID) Prompt Words Library
    Technical HAZOP Guide Words Library
    What If Study (Controls HazOpS) Prompt Library
    Causes of Failure
    Construction HAZOP Guide Words Library

## Slide 3: Planning and Preparation

## Slide 4: Study Type
        1. HAZID – The Broad Lens
        Focuses on macro-level hazards and high-level project opportunities (e.g., site optimisation).
        Return to contents page
2. Technical HAZOP – The Technical Lens
Examines technical integrity and process deviations. Identifies opportunities for:
Design simplification
Reduced maintenance and software changes
Alarm rationalisation impacts
Cybersecurity posture adjustments influencing operability and safety.
3. Construction HAZOP – The Physical Lens
Addresses physical execution and human interaction. Identifies opportunities for:
Installation efficiency
Reduced commissioning downtime.
Confirm the Study Type, there are three study types.
Note: A Construction Study follows the HAZOP methodology but uses a specific set of guide words aligned to the physical, installation, and commissioning hazards present during the construction phase.

## Slide 5: Study Tier
        Tier 1 – Facilitated Study (High Risk):
        Required for projects with complex systems, SIS changes, or multi-contractor simultaneous operations (SIMOPS). These studies must be led by a trained facilitator using IEC 61882 methodology to ensure structured hazard identification and operability analysis.
        Return to contents page
Tier 2 – Project Team Study (Lower Risk):
For projects with minor design changes, isolated energy sources, or single-trade activities. These can be completed by the project team using guide words and prompts provided in this procedure.
Confirm the Study Tier, there are two levels of study, based on project risk and complexity.

## Slide 6: Define the Scope
        Confirm boundaries and assumptions.
        While studies may initially focus on discrete portions of the project or specific equipment, a holistic review must be completed at critical milestones to ensure:
        All process, system, and interface risks are considered collectively.
        Opportunities for design improvement and construction efficiency are captured.
        Identify nodes or activities (link to WBS).
        Return to contents page
Define the study’s breadth and limits to ensure accurate preparation and expectations.

## Slide 7: Prepare Study Materials
Latest project documentation, including:
P&IDs developed to a level that enables a meaningful and accurate study
Layout drawings
SWMS
Lift plans
Project Risk Register (PRR)
Work Health and Safety Management Plans
Environmental Impact Assessments
Other preparation materials:
Prompt sheets for guide words (HAZID, HAZOP, Construction)
Pre‑populate the PRR with placeholder entries for hazards and opportunities
        Return to contents page
  Ensure all technical and planning materials are prepared before the workshop..

## Slide 8: Engage the Facilitator & Scribe
Define the Study:
Confirm facilitator and scribe roles.
Agree on the study scope (boundaries, assumptions, exclusions).
Confirm guide / prompt words.
Confirm whether the What‑If Study (Controls HazOpS) prompt tools will be used.
Confirm whether the Causes of Failure library will be used.
Agree on nodes, blocks, or activities to be reviewed
        Return to contents page
  Align on study method, scope, guide words, and supporting prompt tools.
Check readiness:
Identify any facilitator preferences (e.g., physical PRR visibility, whiteboard access)
Validate design maturity (P&IDs, layout drawings, PRR readiness)
Identify required participants based on scope and nodes.
Identify any essential SMEs.
Logistics:
Confirm facilitator requirements (room setup, dual screens, site walk‑through, technology)
Confirm facilitator availability before scheduling

## Slide 9: Select a Suitable Location
Office-based:
  Best for early‑phase HAZID or design‑focused HAZOP.
  Ensure access to drawings, the PRR system, and conferencing tools.
  Dual screens are highly desirable:
    Screen 1: PRR (participants see their input being captured)
    Screen 2: Context media (site map, P&ID, 3D model, etc.)
  Use a physical “Parking Lot” flipchart for out‑of‑scope items.
  Arrange U‑shaped seating to support discussion and visibility.
        Return to contents page
Site-based:
  Mandatory for Construction Studies or when physical layout influences risk.
  Combine a site walk‑through with an office‑based review session when useful.
  Provide a suitable meeting space (quiet, safe, with power and connectivity).
  Consider and inform:
  PPE requirements
  Inductions or access permits
  Accessibility needs (mobility, emergency exits, temperature, noise)
Hybrid:
Ensure a reliable Teams link for remote participants.
Confirm audio quality and visibility for both in-room and remote attendees.
Avoid:
Rooms with poor acoustics
Noisy or high‑traffic areas
Screens too small for PRR visibility
Remote attendees unable to see drawings
  Identify the optimal venue to maximise participation, visibility, and study effectiveness.
  Choosing the right location improves participation, visibility of information, and the quality of discussion.

## Slide 10: Schedule & Invite
        Before sending the invite:
          Confirm attendance method, venue details, and any site access requirements.
        Before the workshop:
        Ask participants to review pre‑read materials before the session.
        Reconfirm attendance from key roles prior to the workshop; identify and request any required WHS attendee exemptions.
        Ensure all essential stakeholders can attend for the full duration of the study.
        When sending the invite:
        Attach agenda and required documents, such as pre‑read information (P&IDs, layout drawings, SWMS, lift plans, reports, EIA, WHSMP).
        Return to contents page
Set your study up for success through early coordination and clear communication.
        Avoid:
          Missing key roles
          No or incomplete pre‑read
          Confusing venue/access details
          SMEs joining late or leaving early

## Slide 11: Common Pitfalls & How to Avoid Them
        Design & Documentation Pitfalls
        Running the study too early → Ensure design maturity (P&IDs, layouts, PRR readiness) is validated before scheduling.
        Missing or outdated drawings → Confirm latest revisions are available and visible to all participants.
        People & Roles Pitfalls
        Missing key SMEs → Identify required participants early and reconfirm their availability.
        Participants not prepared → Send pre‑reads early and request review before the session.
        Ambiguous roles → Confirm facilitator, scribe, and participant roles before scheduling.
        Scope & Method Pitfalls
        Poorly defined scope or boundaries → Agree scope, nodes/blocks, and guide words with the facilitator in advance.
        Using the wrong prompt tools → Confirm applicable prompt sets (HAZID, HAZOP, Construction, What‑If, Causes of Failure).
        Return to contents page
Support smooth, efficient, high‑quality hazard studies by avoiding these common issues.
        Logistics & Environment Pitfalls
        Inadequate room setup → Use dual screens (PRR + context media) and suitable seating for visibility and engagement.
        Poor remote participation → Ensure stable connectivity and test technology beforehand.
        Unclear venue or access requirements → Confirm logistics early (PPE, inductions, parking, site access).
        Workshop Execution Pitfalls
        Capturing actions after the session → Record actions live in the PRR.
        Side conversations or loss of focus → Use a “Parking Lot” for out‑of‑scope items.
        Over‑analysing non‑credible deviations → Use failure causes to test credibility quickly.
        Drifting outside the agreed scope→ Reinforce scope boundaries and use a Parking Lot for out‑of‑scope items.
        Trying to fix hazards instead of documenting hazards→ Capture the deviation → cause → consequence first, then discuss safeguards and actions.

## Slide 12: 2. Prompt Libraries and Failure Cause Lists

## Slide 13: Hazard & Operability Study Guide & Prompt Words
        Return to contents page
Use prompt questions to:
Stimulate thinking during team discussions
Explore credible deviations, failures, and error paths
Challenge assumptions about design intent, safeguards, and controls
Identify both hazards and opportunities to improve design
Provide consistent coverage across all studies
Structured prompts help ensure no credible hazards or failure modes are overlooked.
HAZID - Broad, conceptual hazard identification.
Use prompt questions when:
Brainstorming early‑phase project risks
Identifying high‑level hazards and system interactions
Reviewing major construction, commissioning, or operational hazards
Thinking about external events (weather, access, logistics)Discussing human and organisational factors
Exploring major energy sources and failure consequences
Prompt questions in HAZID help the team:
Scan for big-picture hazards
Understand what could go wrong at a system or location level
Prioritise major risk areas for detailed study later (e.g., HAZOP)
Use prompt questions when:
Reviewing a node with specific process parameters
Assessing deviations from design intent
Exploring failure modes of equipment, control logic, and instrumentation
Challenging the reliability of safeguards
Identifying abnormal operations or upset conditions
Clarifying operator response expectations
Prompt questions in HAZOP help the team:
Reveal failure modes not visible from P&IDs alone
Evaluate interactions between equipment and controls
Identify weaknesses in sequences, alarms, and interlocks
Improve operability and maintainability
HAZOP - Focused review of design intent, deviations, safeguards, and consequences.

## Slide 14: 2a. Hazard Identification (HAZID) Prompt Words Library

## Slide 15: Hazard Identification (HAZID) Prompt Words Library
        Return to contents page
Category | Parameter | Prompt-word deviation | Prompt Cues
Civil, Structural & Geotechnical | Excavations & Slopes | Collapse | What if dewatering fails? Are inspections frequent and documented?
 |  | Inrush | 
 |  | Saturated | 
 |  | Unprotected | 
 |  | Weather-affected | 
 | Stability & Integrity | Progressive | Are temporary load cases considered? Is monitoring adequate to detect early failure?
 |  | Hidden | 
 |  | Overloaded | 
 |  | Undermined | 
 |  | Deteriorating | 
Contractor & Workforce Management | Contractor Competency | Inexperienced | Do contractors have proven Hydro experience? Are critical roles covered on all shifts? Is competence assessed or assumed?
 |  | Unverified | 
 |  | Misaligned | 
 |  | Underqualified | 
 |  | Overstretched | 
 | Fatigue & Human Limits | Fatigued | Are shift patterns realistic for remote Hydro sites? Are environmental conditions increasing fatigue risk?
 |  | Isolated | 
 |  | Extended shifts | 
 |  | Travel impacts | 
 |  | Heat / cold stress | 
 | Supervision & Control | Insufficient | Is supervision adequate during night or weekend work? Is supervision adequate / near high risk / critical assets? Are supervisors managing too many high-risk activities simultaneously?
 |  | Remote | 
 |  | Inconsistent | 
 |  | Overloaded | 
 |  | Absent | 
Category | Parameter | Prompt-word deviation | Prompt Cues
Control, SCADA & Cyber | Control Authority | Confused | Who has control during commissioning or emergencies? Can remote commands conflict with local actions?
 |  | Dual control | 
 |  | Overridden | 
 |  | Unclear handover | 
 |  | Unauthorised | 
Electrical & Power Systems | HV & Switching | Arc flash | Are switching sequences clear and rehearsed? Are live-work boundaries enforced?
 |  | Incorrect switching | 
 |  | Inadequate clearance | 
 |  | Flood-affected | 
 |  | Unauthorised access | 
 | Temporary Power | Inadequate | Are RCDs tested and logged? Are temporary systems removed when redundant?
 |  | Unprotected | 
 |  | Poorly earthed | 
 |  | Overloaded | 
 |  | Modified | 
Emergency Management & Crisis Response | Emergency Plans | Absent | Do plans cover realistic worst-case scenarios? Are plans usable without power or comms?
 |  | Incomplete | 
 |  | Outdated | 
 |  | Untested | 
 |  | Assumption-based | 

## Slide 16: Hazard Identification (HAZID) Prompt Words Library
        Return to contents page
Category | Parameter | Prompt-word deviation | Prompt Cues
Emergency Management & Crisis Response | Emergency Response Capability | Delayed | Response time for medical, rescue and emergency services, considering remoteness, weather and time of day? Are there enough trained responders, vehicles, rescue gear and first aid equipment on site at all times? What if there are multiple casualties or concurrent emergencies (e.g. flood + injury + fire)? Can responders reach the casualty during flood, bushfire, landslip or night-time conditions? What if emergency equipment (defibs, boats, lighting, alarms) is unavailable or inoperable? Do emergency systems rely on mains power that may be lost during an incident? Are rescuers exposed to secondary hazards (water release, HV, confined spaces)?
 |  | Insufficient | 
 |  | Overwhelmed | 
 |  | Inaccessible | 
 |  | Uncoordinated | 
Environmental & Community | Pollution & Spills | Uncontained | Worst-case spill volumes? Spill response under flood conditions?
 |  | Delayed response | 
 |  | Escalating | 
 |  | Undetected | 
 |  | Repeated | 
Category | Parameter | Prompt-word deviation | Prompt Cues
Hydrology & Water Management | Flood & Extreme Events | Exceeded | What if Probable Maximum Flood occurs during construction? Are trigger levels and evacuation criteria clear?
 |  | Coincident | 
 |  | Rapid onset | 
 |  | Unpredicted | 
 |  | Escalating | 
 | Flow Control | Uncontrolled | Can upstream releases endanger workers downstream? Are communications between operations and site reliable?
 |  | Delayed | 
 |  | Unexpected | 
 |  | Incorrect | 
 |  | Manual override | 
Mechanical & Hydraulic Systems | Gates, Valves & Penstocks | Stuck | Can systems be safely isolated for maintenance? Are manual operations feasible in emergencies?
 |  | Leaking | 
 |  | Unbalanced | 
 |  | Ruptured | 
 |  | Unisolatable | 
Mechanical & Hydraulic Systems | Turbines & Rotating Plant | Overspeed | Are protections active during testing and commissioning? What if load is suddenly rejected?
 |  | Runaway | 
 |  | Misaligned | 
 |  | Overheated | 
 |  | Fatigued | 
Project Governance & Delivery | Change Management | Uncontrolled | Can design or construction changes bypass risk review? Are cumulative small changes increasing risk unknowingly? Are site changes reflected in emergency and operating plans?
 |  | Late | 
 |  | Unreviewed | 
 |  | Informal | 
 |  | Cumulative | 

## Slide 17: Hazard Identification (HAZID) Prompt Words Library
        Return to contents page
Category | Parameter | Prompt-word deviation | Prompt Cues
Project Governance & Delivery | Delivery Model & Governance | Unclear | Are accountabilities for safety and risk clearly defined between Owner, EPC, Principal Contractor? Are there gaps between contractual responsibility and operational control? Does the delivery model discourage early hazard reporting?
 |  | Fragmented | 
 |  | Inadequate | 
 |  | Conflicting | 
 |  | Overly complex | 
Site, Access & Logistics | Access & Egress | Restricted | What happens if access / egress is lost during flood or bushfire? Are emergency escape routes clearly defined and maintained?
 |  | Blocked | 
 |  | Weather-dependent | 
 |  | Unmaintained | 
 |  | Single-point | 
 | Heavy Transport & Lifting | Chain of Responsibility | Are bridges, culverts and roads rated and inspected? Are workers / contractors aware of requirements? Are lift paths protected from public access?
 |  | Clearance issues | 
 |  | Load securing | 
 |  | Overloaded | 
 |  | Poor visibility | 
 |  | Unverified routes | 
 |  | Weather-affected | 
WHS Systems & Controls | Permits & Isolation | Incomplete | Are multiple energy sources correctly isolated? Is the project specific permit structure confirmed and clear to all? Are SIMOPS creating permit conflicts?
 |  | Conflicting | 
 |  | Bypassed | 
 |  | Misunderstood | 
 |  | Ineffective | 
Category | Parameter | Parameter | Prompt-word deviation
WHS Systems & Controls | Procedures & SWMS | Generic | Are procedures suitable written for actual site conditions? Are workers /contractors trained in deviations and abnormal situations?
 |  | Outdated | 
 |  | Unfollowed | 
 |  | Impractical | 
 |  | Unknown | 
 |  | Unverified | 

## Slide 18: 2b. Hazard & Operability Study (HAZOP) Guide Words Library

## Slide 19: Hazard & Operability Study (HAZOP) Guide Words Library
        Return to contents page
Parameter | Guideword | Typical Deviation / Interpretation
Alarms & Interlocks | No | No alarm or trip on deviation
 | More | Nuisance or spurious alarms
 | Less | Reduced alarm sensitivity
 | Other than | Wrong alarm or trip function activated
 | Early / Late | Alarm occurs too soon or too late
Composition & Quality | Other than | Wrong material, contamination, off-spec mixture
 | More | Higher impurity or concentration
 | Less | Dilution, reaction incomplete
 | As well as | Unwanted secondary component present
 | Part of | Partial feed or missing reactant
Containment & Environment | No | Containment lost, leak, vent to atmosphere
 | More | Excessive discharge, overflow
 | Less | Inadequate flow to treatment
 | Other than | Wrong discharge route (storm drain, ground)
Electrical & Power | No | Power failure, circuit isolated
 | More | Overvoltage, overload
 | Less | Undervoltage, brownout
 | Reverse | Wrong phase rotation
 | Other than | Wrong circuit energized
Equipment & Operation | No | Not started, isolated, or failed
 | More | Operating too fast or too often
 | Less | Operating below required capacity
 | Reverse | Wrong direction (e.g., pump reversed)
 | Other than | Wrong equipment operating (e.g., standby unit)
Parameter | Guideword | Typical Deviation / Interpretation
Flow | No Flow | Blocked line, pump failure, valve closed, or empty suction tank
 | More Flow | Pump overspeed, control valve failed open, or reduced downstream pressure
 | Less Flow | Partial blockage (scaling/debris), filter fouling, or pump cavitation
 | Reverse Flow | Check valve (NRV) failure, siphon effect, or higher downstream pressure
 | Misdirected Flow | Wrong valve alignment, bypass left open, or internal leak in a heat exchanger
 | As well as | Unintended secondary flow path or bypass
 | Part of | Partial flow only through part of system
 | Other than | Flow of wrong fluid or medium
 | Intermittent | Pulsating or unstable flow pattern
 | Early / Late | Flow starts or stops at wrong time
Human & Interface | No | No operator action taken
 | More | Excessive intervention, over-adjustment
 | Less | Insufficient response
 | Other than | Wrong control manipulated
 | Late / Early | Operator reacts too late/soon
 | Reverse | Misunderstood direction (open vs. close)

## Slide 20: Hazard & Operability Study (HAZOP) Guide Words Library
        Return to contents page
Parameter | Guideword | Typical Deviation / Interpretation
Flow | No Flow | Blocked line, pump failure, valve closed, or empty suction tank
 | More Flow | Pump overspeed, control valve failed open, or reduced downstream pressure
 | Less Flow | Partial blockage (scaling/debris), filter fouling, or pump cavitation
 | Reverse Flow | Check valve (NRV) failure, siphon effect, or higher downstream pressure
 | Misdirected Flow | Wrong valve alignment, bypass left open, or internal leak in a heat exchanger
 | As well as | Unintended secondary flow path or bypass
 | Part of | Partial flow only through part of system
 | Other than | Flow of wrong fluid or medium
 | Intermittent | Pulsating or unstable flow pattern
 | Early / Late | Flow starts or stops at wrong time
Human & Interface | No | No operator action taken
 | More | Excessive intervention, over-adjustment
 | Less | Insufficient response
 | Other than | Wrong control manipulated
 | Late / Early | Operator reacts too late/soon
 | Reverse | Misunderstood direction (open vs. close)
Parameter | Guideword | Typical Deviation / Interpretation
Flow | No Flow | Blocked line, pump failure, valve closed, or empty suction tank
 | More Flow | Pump overspeed, control valve failed open, or reduced downstream pressure
 | Less Flow | Partial blockage (scaling/debris), filter fouling, or pump cavitation
 | Reverse Flow | Check valve (NRV) failure, siphon effect, or higher downstream pressure
 | Misdirected Flow | Wrong valve alignment, bypass left open, or internal leak in a heat exchanger
 | As well as | Unintended secondary flow path or bypass
 | Part of | Partial flow only through part of system
 | Other than | Flow of wrong fluid or medium
 | Intermittent | Pulsating or unstable flow pattern
 | Early / Late | Flow starts or stops at wrong time
Human & Interface | No | No operator action taken
 | More | Excessive intervention, over-adjustment
 | Less | Insufficient response
 | Other than | Wrong control manipulated
 | Late / Early | Operator reacts too late/soon
 | Reverse | Misunderstood direction (open vs. close)

## Slide 21: Hazard & Operability Study (HAZOP) Guide Words Library
        Return to contents page
Parameter | Guideword | Typical Deviation / Interpretation
Safe Design of Structures - Structural integrity | No / None | Critical load-bearing element omitted from design or not specified
 | Less | Strength, stiffness or capacity is less than required for design loads
 | More | Structural demand exceeds assumptions due to additional or unforeseen loads
 | Part of | Structural system only partially complete or relies on temporary stability
 | As well as | Additional loads introduce (plant, storage, change of use)
 | Reverse / Opposite | Load paths act in an unexpected direction (uplift, lateral, impact)
 | Other than | Structure used for a purpose not considered in design intent
Safe Design of Structures - Environmental loading | More | Wind, seismic, flood or fire loads exceed design basis
 | Less | Environmental effects underestimated or ignored
 | As well as | Combined environmental actions not considered together (e.g. wind + rain)
 | Other than | Different environmental conditions than assumed (microclimate, terrain)
Safe Design of Structures - Construction sequencing | Early | Structural element loaded before adequate strength or support achieved
 | Late | Temporary supports or stabilisation removed too late, creating hazards
Parameter | Guideword | Typical Deviation / Interpretation
Safe Design of Structures - Construction sequencing (continued) | No / None | No defined construction methodology or sequencing provided
 | Part of | Only part of the structure is stable during erection
 | Faster | Accelerated construction increases instability or worker exposure
 | Slower | Prolonged temporary conditions introduce additional risks
Safe Design of Structures - Temporary works | No / None | Temporary works not designed or documented
 | Less | Temporary works inadequately designed for applied loads
 | More | Temporary loads exceed assumed capacity
 | Other than | Temporary works altered on site without design review
Safe Design of Structures - Access & egress | No / None | No safe access provided for construction, use or maintenance
 | Less | Access is restricted, unsafe or does not meet ergonomic needs
 | More | Additional access required due to unplanned tasks or activities
 | Other than | Access routes used differently than intended (climbing, shortcuts)

## Slide 22: Hazard & Operability Study (HAZOP) Guide Words Library
        Return to contents page
Parameter | Guideword | Typical Deviation / Interpretation
Safe Design of Structures - Work at height | No / None | No fall prevention or fall protection integrated into design
 | Less | Edge protection, anchorage or barriers inadequate
 | Part of | Protection provided in some areas only
 | As well as | Additional fall hazards introduced by equipment or layout changes
Safe Design of Structures - Maintenance & servicing | No / None | No consideration of maintenance access or future servicing tasks
 | Less | Access is difficult, awkward or unsafe, increasing manual handling risk
 | More | Maintenance activities more complex or frequent than anticipated
 | Other than | Maintenance performed using alternative methods due to poor design access
Safe Design of Structures - Human interaction | Less | Ergonomic considerations insufficient (posture, reach, force)
 | More | Greater manual handling effort required than assumed
 | As well as | Simultaneous tasks create interaction or interface hazards
 | Other than | Workers interact with structure in unintended ways
Safe Design of Structures - Materials selection | No / None | Hazardous material risks not identified or addressed
 | More | Materials introduce increased fire, toxicity or handling risk
 | Less | Durability or protective treatment inadequate
 | Other than | Alternative materials substituted without design reassessment
Parameter | Guideword | Typical Deviation / Interpretation
Safe Design of Structures - Interfaces (systems / trades) | No / None | Interfaces between structural and other systems not defined
 | Less | Coordination between trades insufficient, creating clashes or hazards
 | As well as | Additional systems added increasing load or access complexity
 | Other than | Systems installed differently than assumed in design
Safe Design of Structures - Information & documentation | No / None | No safety-critical information provided in drawings or specs
 | Less | Safety information unclear, incomplete or ambiguous
 | Late | Safety information provided too late to influence construction
 | Other than | Documentation interpreted differently by downstream users
Safe Design of Structures - Use & occupancy | More | Occupancy or usage exceeds design assumptions
 | Less | Design restricts safe use or movement of occupants
 | Other than | Change of use not considered in original design
Safe Design of Structures - Modification & demolition | No / None | Demolition or modification risks not considered in design
 | Less | Structural behaviour during removal not adequately addressed
 | Other than | Unplanned modifications create instability or exposure

## Slide 23: Hazard & Operability Study (HAZOP) Guide Words Library
        Return to contents page
Parameter | Guideword | Typical Deviation / Interpretation
Temperature | High | Loss of cooling water, heater control failure, or exothermic reaction
 | Low | Loss of heating, Joule-Thomson cooling (gas expansion) or ambient freezing
 | None | No heat input, heater off
 | More | Overheating or thermal runaway
 | Less | Cooling too much or heat loss
 | Reverse | Heat transfer reversed, cross-contamination
 | Other than | Wrong temperature control loop in service
Utilities | No | Utility not available or supply failed
 | More | Over-supply, overpressure, excessive cooling
 | Less | Insufficient supply or pressure
 | Other than | Wrong utility connected (e.g., air instead of nitrogen)
 | Intermittent | Unstable or unreliable supply
Valve & Isolation | No | Valve not opened or closed as required
 | More | Excessive opening, leakage
 | Less | Valve throttled or restricted
 | Reverse | Flow direction opposite intended
 | Other than | Wrong valve operated
 | As well as | Multiple valves open simultaneously

## Slide 24: 2c. What If Study (Controls HazOpS) Prompt Library

## Slide 25: What If Study (Controls HazOpS) Prompt Library
        Return to contents page
Controls system and logic to be broken into blocks and the Hazards (Risk areas) discussed (e.g. prevention of over speed, excessive pressure rise, penstock pulsations, over / under voltage etc.). Then ‘What If’ questions applied to each block.
‘What if’ questions should be constructed considering the three basic categories of causes of accidents:
Equipment Failures;
External Events; and
Human Error
There are also some overview categories listed on the following slides.
Hazard Study Job Manager /and/or Facilitator to select appropriate questions from the list in conjunction with Asset and/or Project Engineer.

## Slide 26: What If Study (Controls HazOpS) Prompt Library
        Return to contents page
Category | Question
Controls | there is a loss of power supply there is a complete loss of signal there is a control system mechanical failure there is a control system software failure there is a control system operator error there is a control system logic error
PLC’s | there is a PLC power supply failure there is a PLC software error the PLC output freeze there is a MMI input error. there is a loss or change of input signal there is an unplanned reboot / planned reboot
Batteries / UPS | Batteries / UPS there is a loss of output there is a low voltage there is a loss of capacity (deterioration or additional demand)
Communications | there is a loss of link
Alarms | an alarm fails an alarm activates spuriously an alarm is disregarded an alarm is disabled alarms are inadequate alarms cannot be seen alarms cannot be heard
Transmitters | a transmitter fails a transmitter sends an incorrect signal
Equipment Failures
Category | Question
Components | a component ruptures (e.g. pipes, vessels) a component leaks (e.g. pumps, valves) a component blocks (e.g. pipes, tubes) a component fails open (e.g. valve) a component fails closed (e.g. valve) a component fails to open on demand (e.g. valve) · a component fails to close on demand (e.g. valve) a component fails to start (e.g. pump) a component fails to stop (e.g. pump) a component starts prematurely (e.g. pump) a component stops prematurely (e.g. pump) a component over speeds (e.g. driver on engine) a component loses heating / cooling (e.g. exchangers) a component structure becomes corroded, weakened, etc. a component is not maintained / cleaned
Instrumentation | instrumentation fails instrumentation reads inaccurately (e.g. high, low) instrumentation is calibrated improperly instrumentation is incorrectly installed instrumentation is improperly located instrumentation loses all power instrumentation loses partial power instrumentation receives inadequate maintenance instrumentation measures the wrong factor instrumentation is subjected to electrical noise / surges a set point is wrong (e.g. high, low)

## Slide 27: What If Study (Controls HazOpS) Prompt Library
        Return to contents page
Category | Question
Sensors | a sensor fails a sensor blocks or is fouled a sensor is inappropriately located
Displays | a display sticks a display zero is misadjusted a display is misread a display cannot be seen
Filters | filter blocks filter overpressures filter fails to function filter ruptures filter has a screen installed with an incorrect mesh size
Piping | piping leaks piping is fractured piping blocks piping becomes fouled piping is corroded internally piping is corroded externally piping is eroded piping supports fail piping is subject to external impact piping is subject to backflow piping is subject to flow or pressure surges piping is subject to liquid hammer piping is subject to vibration welds leak gaskets / seals / flanges leak pressure relief fails (open / closed) sight glasses break
Equipment Failures, continued
Category | Question
Valves | valve fails mechanically valve actuation fails valve is misoperated valve leaks valve seals fail valve becomes fouled or corroded valve is subjected to flow or pressure surges valve is subjected to liquid hammer valve is impacted externally valve is subjected to backflow
Motors | there is a short circuit the motor overheats there is a loss of power
Bunding | the capacity of the bund is insufficient the bund's wall strength is insufficient the bund is flooded the bund is too close to the tank the bund is damaged

## Slide 28: What If Study (Controls HazOpS) Prompt Library
        Return to contents page
Category | Question
Pumps | pump fails to start / stop on demand pump is started with the discharge isolation valve closed pump is started with the suction-side valve closed pump relief valve fails open / closed pump loses suction / has too low a NPSH pump becomes vapour locked, cavitates pump packing gland or seal leaks pump is subjected to freezing pump is submerged under water pump over speeds pump under speeds pump isn't maintained, cleaned pump breaks a shaft pump loses lubrication pump's power supply fails
Tanks | tank leaks tank is overfilled tank vent blocks tank relief valve fails (open / closed) tank heating / cooling system fails (high / low) tank filling / emptying line breaks tank lining becomes corroded, weakened, fails tank instrumentation fails tank is exposed to high temperature (e.g. external fire) tank is not cleaned, maintained tank is over pressured
Equipment Failures, continued
Category | Question
Heat Exchangers | heat exchanger loses its cooling flow heat exchanger's relief valve fails open / closed heat exchanger is over pressured heat exchanger leaks from high to low pressure side heat exchanger tube ruptures heat exchanger has too high flow rate heat exchanger has too low flow rate heat exchanger's tubes are subjected to vibration heat exchanger experiences excessive fouling (either side) heat exchanger isn't cleaned, maintained
Pressure Relief / Anti Vacuum Valves | the valve activates prematurely the valve fails open the valve fails closed the valve chatters the valve is set to open at an improper pressure the valve blocks the valve has a high back pressure the valve has a spring failure

## Slide 29: What If Study (Controls HazOpS) Prompt Library
        Return to contents page
Category | Question
Natural Events - WEATHER | the ambient temperature is extreme (high / low) (may cause vaporization or freezing of materials, thermal stresses or embrittlement) a forest or bush fire occurs a plant fire occurs flooding external to the plant occurs flooding occurs within the plant frost occurs hail occurs a severe storm occurs ice forms on structures during cold weather lightning occurs during a storm a mud slide occurs it rains or the weather is very humid sleet occurs it snows there is solar radiation there is a static electricity build-up there are high winds
Natural Events - GEOLOGIC | there is earth movement there is an earthquake there is a landslide there is severe erosion in the vicinity of the plant
2. External Events
Category | Question
Human Induced Events – TRANSPORTATION | there is a vehicle accident (car, truck) there is a crane accident there is a lifting device accident there is a fork lift accident
Human Induced Events - ADJACENT OPERATION | there is a system disturbance there is an incident in an adjacent unit there is construction in the vicinity there are dropped objects there is a fire in an adjacent unit there is leakage of Hazardous chemicals in the area there are loading / unloading operations in the vicinity a missile is set off (compressed gas cylinders, rotating equipment, explosions) there is smoke in the area there is a structural failure
Human Induced Events - MAINTENANCE ACTIVITIES | cutting is performed during maintenance lifting is performed during maintenance temporary stresses occur during maintenance welding is done during maintenance
Human Induced Events - DELIBERATE | someone sabotages the plant someone vandalizes the plant there is a terrorist act
External Events originate outside the facility but can often have an adverse effect on it. Typical questions concerning External Events, categorized by type, are provided here:

## Slide 30: What If Study (Controls HazOpS) Prompt Library
        Return to contents page
Category | Question
Utility Failures | the buildings air system fails the assets/equipment's air system fails the breathing air system fails the cooling water system fails the electrical system fails the electric heating system fails the electric heat tracing system fails the lube oil system fails the dewatering system fails the fire water system fails the backup utility systems fail
2. External Events, continued

## Slide 31: What If Study (Controls HazOpS) Prompt Library
        Return to contents page
Category | Question
General | improper design is used improper construction is performed improper start-up procedures are used inadequate operating procedures are used inadequate Emergency procedures are used improper maintenance is performed improper testing is performed improper inspection is performed improper decommissioning procedures are used improper demolition procedures are used management is inadequate or unsatisfactory
Operators | Operator does not perform an action Operator performs the wrong action Operator performs an action at the wrong time Operator performs an action at the wrong place Operator performs actions in the wrong sequence
Maintenance | maintenance is not done regularly maintenance is done improperly maintenance is done at the wrong time maintenance does not restore the component to normal working conditions maintenance inadvertently initiates a future Hazardous condition
3. Human Error
Category | Question
Testing | testing is done improperly testing is not done thoroughly / realistically testing is done irregularly
Research across high‑risk industries indicates that human factors contribute to a substantial proportion of accidents. For this reason, it is essential that potential human error is considered during hazard analysis. The types of errors that designers, operators, maintenance personnel, and supervisors may make depend on the specific task and operational context. The following prompts provide examples of human error types and common contributing factors to assist analysts in developing study‑specific questions.

## Slide 32: What If Study (Controls HazOpS) Prompt Library
        Return to contents page
Category | Question
Miscellaneous | Earthing Lighting protection Equipment environment Spares Testing Training
Software | QA Revision Control Testing and Commissioning
Maintenance | Isolation Manual override Offline requirements
Documentation | Design philosophy Operating Instructions Standard Operating Procedures Abnormal operating procedures Software design and documentation Commissioning
4. Overview

## Slide 33: 2d. Causes of Failure

## Slide 34: Causes of Failure
        Return to contents page
Use Causes of Failure whenever the team needs to confirm whether a deviation is credible, understand why it could happen, or determine how it should be controlled.
When to Use “Causes of Failure”
After Identifying a Deviation
Once the team agrees a deviation is credible (e.g., More Flow), the next step is to identify specific causes, such as:
Control valve failed open
Pump overspeed
Incorrect setpoint
Operator error
This happens before considering consequences or safeguards.
2. To Determine Credibility
If the team cannot identify a realistic cause:
The deviation is considered not credible, and
No further analysis (consequences / safeguards / actions) is required.
Clearly identifying causes keeps the study efficient and focused.
To Tailor Safeguards
Safeguards must address the actual cause, not the deviation alone.
Examples:
Cause = Human error → Safeguard may be training, procedures, or HMI improvements
Cause = Mechanical failure → Safeguard may be redundancy, alarms, or condition monitoring
Cause = Logic or software fault → Safeguard may be validation, interlocks, or testing
Understanding the cause drives the right control or improvement.

## Slide 35: Causes of Failure
        Return to contents page
Causes of Failure Lists
These lists can be used to:
Support HAZID and HAZOP “What If” discussions
Prompt the team to consider common failure modes
Ensure consistency across nodes and facilitators
Recommended Use
Use the short list to guide discussion during the workshop
Use the full detailed list as a reference, not a checklist
Apply only the causes relevant to the system and node under review
Cause lists should stimulate thinking-not replace engineering judgement.

## Slide 36: Causes of Failure
        Return to contents page
Category | Prompt Cue
Natural Events - Weather | barometric pressure, rapid changes during hurricanes and severe storms drought, may impact the availability of cooling water for plant site dust storm extreme ambient temperature (high / low) vaporization or freezing of materials, thermal stresses or embrittlement may occur fire (forest / bush) check proximity to trees and combustible vegetation fire (plant) review proximity to flammable-containing systems, e.g. fuel oil storage flooding (external) rivers, lakes, streams, ocean, storm water drainage fog frost, may cause damage to foundations hail, has potential for missile impacts hurricane ice, loss of cooling, mechanical damage due to falling ice lightning, may damage plant power system, computer control systems are vulnerable mud slide pollution rain or high humidity sleet smoke snow, may result in overloadings static electricity wind (high), both pressure and missile effects wind (turbulent)
Category | Prompt Cue
Instrumentation | sensor fails transmitter fails inaccurate reading (high, low) set point wrong
Controls | power fails logic error control lines severed incorrect command
Components - Pipes | internal corrosion external corrosion erosion chemical attack cracks external impact vibration liquid hammer overpressure poor welds inadequate support overloading fouling sight glass breaks
Components - Vessels | cracks seal failure flange leaks agitator failure overpressure
Components - Valves | flange leak packing leak fouling stem damage power failure
Category | Prompt Cue
Natural Events | earthquake landslide tsunamis
Aging Plant | corrosion metal fatigue sinking foundations Compliance internal standards not met redundant piping / equipment lack of maintenance failed pipe / vessel supports mindsets in operators wiring insulation failed embrittlement of seals, packings, gaskets settling wear out of components building integrity / deterioration
Components | ruptures (e.g. pipes, vessels) leaks (e.g. pumps, valves) blocks (e.g. pipes, condensers) fails open (e.g. valve) fails closed (e.g. valve) fails to open on demand (e.g. valve) fails to close on demand (e.g. valve) fails to start (e.g. pump) fails to stop (e.g. pump) incorrect element (e.g. impeller) overspeeds (e.g. driver on engine) loss of heating / cooling (e.g. exchangers)

## Slide 37: Causes of Failure
        Return to contents page
Category | Prompt Cue
Components - Pumps | seal leak gland leak bearing failure impeller imbalance cavitation vapor lock overheating gasket failure scaling overspeed power failure
Components - Compressors | seal leak backflow damages tubing overpressure loss of power explosion overspeed overheats freeze
Components - Exchangers | fouling / plugging loss of cooling loss of product leaks overpressure corrodes
Components - Filters | blocks corrodes through comes loose
Category | Prompt Cue
Safety Devices - Pressure / Vacuum Relief Valve | activate prematurely fails open fails closed chatter improper set pressure blocks high back pressure spring failure bellows failure
Safety Devices - Rupture Disks | installed backwards wrong pressure rating corrodes through not seated properly
Safety Devices - Flame Arrester | plugged damaged
Safety Systems - Bunds | capacity insufficient wall strength insufficient flooded too close to tank damaged
Safety Systems - Water Sprays | plugged internal corrosion wrong orifice poor distribution pattern inadequate water supply spray blocked
Category | Prompt Cue
Components - Heaters | loss of power Overheats
Components - Flare | flame failure igniter failure blocks liquid carryover undersized
Components - Columns | clogged tray collapsed tray faulty tray plugged drain cover
Instrumentation - Sensors | blocks mechanical failure improperly located incorrectly installed
Instrumentation - Transmitters | loss of instrument air mechanical failure
Instrumentation - Displays | sticks zero misadjusted
Controls | utility failure mechanical failure computer failure operator error

## Slide 38: Causes of Failure
        Return to contents page
Category | Prompt Cue
Safety Systems - Gas Detector | poisoned circuit fault wrong type damaged
Safety Systems - Barriers | undersized damaged
Machinery - Motors | short circuit overheating loss of power
Human Induced - Transportation (Movement, Incident, Crash) | airplane marine railroad vehicle crane lifting device fork lifts
Human Induced - Maintenance Activities | crimping pipes cutting lifting temporary stresses welding
Human Induced Events - Deliberate | sabotage vandalism
Category | Prompt Cue
Human Induced Events - Adjacent Operations | adjacent process units construction dropped objects external fire flooding [internal] - failure of water storage tank, blockage of storm water sewer leaking chemicals - may impair operators, equipment damage possible loading / unloading operations missiles / Projectiles - compressed gases, rotating equipment, explosions (pressure vessels, vapors / gases) nearby plants / processes outside Contractors pipelines storage facilities structural integrity toxic vapor release - may impair operators

## Slide 39: Causes of Failure
        Return to contents page
Category | Prompt Cue
Categories of Error | action is not performed (omission error). action is performed incorrectly. action is performed in wrong place. action is performed at wrong time. action is performed in wrong sequence. non-required action is performed (commission error).
Actions | design construction commissioning operation maintenance sampling testing inspection emergency response start up shut down decommissioning demolition
Types of Errors | slips or aberrations those due to poor training or instructions those due to lack of physical or mental ability those due to a deliberate decision not to follow directions (violations) those due to actions, inactions or decisions by managers (management errors)
Category | Prompt Cue
Violations | disgruntled Worker overzealous Worker short cuts in operations correct procedures are tedious correct procedures do not appear to make sense makes work easier emphasis on wrong goals
Management Errors | managers not designated no policies and procedures no implementation of policies and procedures resources not allocated no commitment mismatch of responsibility, authority and accountability no lines of authority no planning or scheduling no performance standards, measures or controls inadequate communication no auditing
Category | Prompt Cue
Reasons for Errors | slips or aberrations inattention to operation distracted Worker training or instructions inadequate training inadequate supervision poor instructions poor procedures training or instructions not understood no regular refresher training physical or mental ability equipment not accessible inadequate strength inadequate vision inadequate hearing inadequate reading skills poor memory does not understand job overwork boredom habits mindsets inability to handle unusual situation Worker has unrealistic objectives Worker does not follow instructions well poor communication skills
Human Error

## Slide 40: Causes of Failure
        Return to contents page
Category | Prompt Cue
Utility Failure | air (factory, admission, breathing) backup systems cooling water electricity fuels (fuel gas, natural gas, propane, bunker C, heating oil, gasoline, kerosene, diesel) fume / dust / vapor collection heating medium (steam, electricity, transfer oil, molten salt) heat tracing (steam, electric) incineration inert gas inerting oil (flush, lube, seal, mineral, heat transfer) pressure / Vacuum System purge gas radioactivity (NDT, level devices) sewer (chemical, sanitary, storm) steam ventilation / exhaust water
Category | Prompt Cue
Location of Workers | proximity to Hazards duration of exposure to Hazards
Location of Control Room / Station and Other Buildings / Work Areas | ability to withstand and / or protected from toxic material releases overpressure thermal radiation collapse of tanks, vessels, or other structures impact by vehicle flooding by Hazardous liquids able to be sealed - positive pressure sewers sealed control room ventilation isolability from outside air emergency breathing air capability adequate Emergency exit(s) Note: consider areas where Workers may congregate or work, e.g. local operating stations for equipment loading / unloading areas utility operating stations guard houses and security stations engineering workshops Contractor work areas laboratories maintenance shop stores lunch / break rooms and cafeteria administrative spaces
Category | Prompt Cue
Site Layout | topography drainage adjacent facilities buffer zones (EPA) population density (EPA) emergency response access evacuation routes aircraft and trains
Facility Layout | first aid / medical stations accessibility access for construction adjacent operations location of services domino effects location of ignition sources
Unit Layout | access for operations access for maintenance pipelines pipe racks access for Emergency response established spacing guidelines employed separation of Hazards stacking of equipment above Hazardous equipment surge storage capacities minimized electrical classification
Storage Layout | bunding and drainage tank-to-tank spacing downwind of ignition sources temporary storage is suitable inventories minimized
Human Error
Site and Facility Layout Note: The following are some general facility siting issues.

## Slide 41: Causes of Failure
        Return to contents page
Category | Prompt Cue
Emergency Response and Firefighting Capabilities | location of detection devices access for Emergency responders and their equipment access by fire or Emergency vehicles onsite Emergency Workers equipped and trained sufficient PPE PPE properly located firewater supplies sufficient adequate firewater pressure & distribution system appropriate power supplies for firewater pumps vulnerability of fire-fighting and Emergency Response systems and equipment command centre located away from Hazards escape routes safe havens
Toxic Vapor Release Events | toxic gas detectors ventilation intakes isolability emergency breathing systems devices available to indicate wind direction to unit / plant Workers - visible at night plant alarms evacuation routes and muster points effects on visibility
Secondary Containment | bunding collection points
Site and Facility Layout

## Slide 42: 2e. Construction Study (HAZOP) Guide Words Library

## Slide 43: Construction Study (HAZOP) Guide Words Library
        Return to contents page
Category | Guide Word | Prompt Cues
Emergency & Crisis | Major Incident Escalation | Media Regulator Client coordination
 | Evacuation Of Vulnerable Persons | Mobility-impaired Visitors
 | Health Outbreaks | Pandemic response Isolation PPE
Environmental & Heritage | Chemical & Spill Management | Chemical storage and secondary containment Hazardous chemicals onsite Refuelling areas (bunded) Spill response drills
 | Climate & Weather Hazards | Climate resilience measures - flood risk Heat stress Bushfire risk Rainfall/runoff impacts Seasonal environmental constraints
 | Land & Water Protection | Contaminated land management Drainage and waterway protection Ground and aquatic disturbance Groundwater protection measures Microplastic pollution Sediment and erosion control Washdown areas
 | Air, Noise & Light Pollution | Dust suppression during earthworks Noise and air quality Noise/vibration impact on nearby residents Light pollution affecting wildlife
 | Environmental Management Systems | Environmental incident reporting procedures Environmental monitoring Environmental training for workers
Category | Guide Word | Prompt Cues
Environmental & Heritage (continued) | Biodiversity & Habitat | Flora/fauna disturbance Vegetation clearing protocols Weed management Wildlife movement corridors
 | Heritage & Visual Impact | Heritage buffer zones and signage Heritage site protection Visual impact
 | Sustainability & Waste Management | Site rehabilitation planning Use of biodegradable or low-impact materials Waste segregation and disposal
 | Other Environmental Hazards | Community health Legacy environmental risks Microplastic pollution Invasive species risks Ecological connectivity

## Slide 44: Construction Study (HAZOP) Guide Words Library
        Return to contents page
Category | Guide Word | Prompt Cues
Integrated & Hazards | Structural & Engineering Compliance | Engineering certification Structural integrity checks Structural integrity (demolition) Propping and collapse risk Exclusion zones
 | Plant, Equipment & Tools | Mobile plant standards Operator competency Reversing and collision risks Unguarded moving parts Equipment inspections Equipment parking near sensitive areas Forklift/pedestrian separation Interaction with overhead loads Lighting and visibility aids Station assets (cranes, pressure vessels) Test and tag requirements Pre-start checks and logbooks Correct tool use PPE requirements Maintenance and inspection Hytorc spanner - incorrect fittings, training and competency
 | Electrical & Earthing Hazards | Live panels and arc flash PCB and SF6 handling Induction and qualifications External party coordination Switchyard and pipework Trailing and working earths
 | Manual Handling & Ergonomics | Ergonomics and repetitive tasks Twisting, ducking, lifting Mechanical aids Safe storage and walkways
Category | Guide Word | Prompt Cues
Integrated & Hazards (continued) | Environmental & Hygiene Hazards | Changing site conditions Waste removal and sanitation Environmental hygiene (dust, mud)
 | Human Factors & Behavioural Risks | Leadership influence Behavioural compliance Fatigue, stress, distractions (cumulative risk) Language barriers Unclear instructions Scope changes Workforce turnover
 | Worksite Interfaces & Coordination | Multi-contractor/trade hazards Interface with operational assets Simultaneous operations
 | Temporary Works & Stability | Scaffolding collapse Formwork failure Bracing issues Temporary structures Trench collapse Lifting gear failure Temporary works stability
 | Hot Work & Fire Safety | Fire extinguisher and water tanker Grinding and welding Fire bans and permits Evacuation routes Combustible materials Fire drills Fire watch
 | Weather & Environmental Conditions | Extreme weather impact on cranes, scaffolding, lifts Thermal expansion/contraction Ice, snow, lightning Shelter and shade

## Slide 45: Construction Study (HAZOP) Guide Words Library
        Return to contents page
Category | Guide Word | Prompt Cues
Integrated & Hazards (continued) | Specialised Operations | Cranes - ground failure, lift studies, overhead hazards Helicopter - landing, refuelling, rigging Diving - depth, pressure, air source contamination Painting - lead/chromium paint, grit blasting, overspray Water - boating, drowning, inundation risks
 | Site Clean-Up & Rehabilitation | Remaining hazards Rubbish and waste Rehabilitation and drainage Road condition restoration
 | Consumables & Supply Chain | Availability and delivery frequency Stock levels and ordering
Legal & Insurance | Insurance Coverage & Claims | Exclusions Delays Claims process
 | Regulatory Compliance & Changes | New codes Standards Permits
 | Contractual Risk & Scope Management | Ownership of risk Scope gaps
Lifecycle | Design Phase Hazards | Constructability risks Access limitations Maintenance challenges
 | Commissioning Risks | Incomplete systems Training gaps Handover delays
 | Decommissioning Hazards | Legacy services Structural integrity concerns Demolition risks
Category | Guide Word | Prompt Cues
Logistics & Transport | Loading & Unloading | Communication protocols between operators and spotters Contractor interaction risks Exclusion zones – barriers, spotters, signage Ground compaction and reinforcement – mats, gravel, steel plates Lift planning and sequencing Lighting for early morning or night operations Load stability and centre of gravity checks Manual handling risks and controls Mobile plant and crane operations Rigging equipment checks Storage planning (short/long term) Uneven or soft ground Vehicle turning and reversing Weather protection for sensitive loads – tarps, shelters, elevated platforms
 | General Transport | Coordination with crane/lift plans Coordination with other site activities Coordination with public transport/pedestrians Delivery schedules Driver induction and site rules Load securing procedures Load weight verification – axle limits, overloading risks Oversized load transport planning and contact points Staging areas for incoming deliveries Temporary storage near sensitive areas

## Slide 46: Construction Study (HAZOP) Guide Words Library
        Return to contents page
Category | Guide Word | Prompt Cues
Logistics & Transport (continued) | General Transport (continued) | Traffic management plan for deliveries Vehicle loading/unloading during adverse weather Vehicle loading/unloading working at heights (e.g. on trailer) Weather-related transport delays and contingencies – alternate plans, notifications
 | Hazardous Goods Transport | Dispatch and receipt inspection of loads Driver training and licensing for hazardous goods Emergency response plans – spills, fire, exposure Hazardous goods segregation during transport Quantities onsite Regulatory compliance Specific transport requirements Transport route risk assessment Vehicle signage and placarding requirements
Planning & Documentation | Job Planning & Coordination | Conflict between contractors Contingency planning for delays or disruptions Critical and sensitive tasks Design change impacts – late revisions, scope creep Documentation version control – outdated drawings or procedures Handover documentation verification Interface hazards between trades Interface with operational assets – live systems, shutdown coordination Lessons learned from similar projects Permit-to-work coordination – overlapping permits, approvals, and controls Planning for inspections and hold points
Category | Guide Word | Prompt Cues
Planning & Documentation | Job Planning & Coordination (continued) | Pre-start planning meetings and attendance Remote work risks Shortcuts and rushed work Simultaneous operations Work sequencing and staging risks
 | SWMS & Risk Assessment Development | Hazard capture and control planning Observation of new worker practices Risk assessment updates for scope changes – variation, new equipment, new trades Site visits before mobilisation SWMS audit and compliance checks – scheduled reviews, corrective actions SWMS review and approval process
 | Interface with External Projects & Stakeholders | Adjacent projects – vibration, access, shared utilities Stakeholder interface – expectations, communication breakdowns Third-party contractors – overlapping scopes, shared access zones

## Slide 47: Construction Study (HAZOP) Guide Words Library
        Return to contents page
Category | Guide Word | Prompt Cues
Regulatory, Stakeholder & Engagement | Regulatory Approvals & Notifications | Approvals to start work External permits (planning, building, environmental) WorkSafe notifications (asbestos, lead) Transport authority notifications - traffic management plans, road closures Utility providers coordination - water, gas, telecoms DSG road access approvals TasNetworks coordination
 | Heritage & Environmental Coordination | Aboriginal and cultural heritage notifications Heritage Tasmania coordination – heritage-listed sites Threatened species management plans Seasonal work restrictions - breeding seasons, migratory species Environmental incident reporting protocols - spills, breaches
 | Community & Stakeholder Engagement | Community engagement sessions for disruptive works Notifications to landowners, stakeholders, and public Public event coordination Local council notifications - public space impacts Marine and waterway authority notifications
 | Emergency & Adjacent Project Coordination | Emergency services coordination - fire, ambulance, police Neighbouring project coordination - conflict avoidance
Category | Guide Word | Prompt Cues
Regulatory, Stakeholder & Engagement (continued) | Service Identification & Access | Service locations and types Service identification signage and barriers - colour coding, warning tape Confined/energised service access Dial Before You Dig (DBYD) Depth and clearance verification - potholing, hand digging Unmarked or undocumented underground services
 | Service Hazards & Legacy Risks | Gas, water, or steam pipe hazards Non-standard electrical cabling risks Overhead power lines Legacy or redundant service risks Pipework and chambers
 | Service Isolation & Protection | Service isolation and lockout/tagout Service relocation or protection planning - temporary rerouting, shielding Temporary service disconnection impacts - water, power, comms
 | Service Setup & Reinstatement | Temporary power or lighting setups Service reinstatement planning post-construction - testing, commissioning

## Slide 48: Construction Study (HAZOP) Guide Words Library
        Return to contents page
Category | Guide Word | Prompt Cues
Site, Establishment & Infrastructure | Amenities & Facilities Planning | Access for inspection and maintenance Accessibility compliance Amenity capacity planning Amenity relocation planning Location planning for amenities Office, crib room, toilets, change rooms Plumbing and electrical setup HVAC and ventilation systems Temporary shelter structures Temporary power supply planning First aid room setup and access
 | Amenity Maintenance & Hygiene | Amenity cleaning frequency - consider workforce size and shift patterns Cleaning schedules and consumables Waste management systems Water supply and quality checks Site drainage planning to prevent water pooling
 | Amenity Comfort & Environmental Control | Break area shading and weather protection Lighting for night works Noise and dust control near amenities Noise mitigation measures during site setup
 | Laydown Area Setup & Management | Drainage and erosion control Dry storage areas Dust suppression measures Equipment parking zones Fire risk management Fuel storage tanks and spill containment Hazardous material segregation Laydown area demarcation and signage Laydown area traffic flow planning
Category | Guide Word | Prompt Cues
Site, Establishment & Infrastructure (continued) | Laydown Area Setup & Management (continued) | Lighting and visibility Noise management from laydown activities Segregation of reusable vs waste materials Stockpile areas (soil, gravel) Temporary bunding for fuel and chemical storage Temporary stormwater management for site run-off Weather protection for sensitive materials
 | Amenity Comfort & Environmental Control | Break area shading and weather protection Lighting for night works Noise and dust control near amenities Noise mitigation measures during site setup
 | Laydown Area Setup & Management | Drainage and erosion control Dry storage areas Dust suppression measures Equipment parking zones Fire risk management Fuel storage tanks and spill containment Hazardous material segregation Laydown area demarcation and signage Laydown area traffic flow planning Lighting and visibility Noise management from laydown activities Segregation of reusable vs waste materials Stockpile areas (soil, gravel) Temporary bunding for fuel and chemical storage Temporary stormwater management for site run-off Weather protection for sensitive materials

## Slide 49: Construction Study (HAZOP) Guide Words Library
        Return to contents page
Category | Guide Word | Prompt Cues
Site, Access & Security | Access Management | Access for inspection and audit teams Access for oversized vehicles Access for subcontractors and deliveries Access for utilities and service providers Contractor access approvals Gate intercoms, swipe cards, keys Induction requirements for access Out-of-hours access permissions Road condition surveys (pre/post) Security codes and WIFI access Weather-related access restrictions
 | Security Systems & Controls | CCTV installation Coordination with local law enforcement Cybersecurity Delivery scheduling to avoid congestion Drone surveillance Emergency vehicle access routes Hazardous materials access control Incident reporting Lighting for security Locking systems and access control Public access prevention Security guards and patrol schedules Temporary signage for hazards and restricted zones Traffic control on-site and near entrances Vandalism and theft risk Visitor induction and escort requirements
Category | Guide Word | Prompt Cues
Site, Access & Security (continued) | Fencing & Physical Barriers | Existing gate modifications Fence height and material specifications Fence integrity inspections New gate locations and locking mechanisms Noise attenuation fencing Temporary fencing installation Visual screening Wildlife exclusion fencing
 | Delineation & Zoning | Delineation for emergency egress routes Dynamic delineation systems High-visibility markings Pedestrian vs vehicle separation Restricted access zones Signage for directional flow Temporary barriers and cones Work zones and exclusion areas
Technology & Systems | Remote Monitoring & Visibility | Loss of visibility Delayed response
 | Digital Systems & Cybersecurity | Software failures Cyber threats AI system errors Remote override issues
 | Automation & Smart Equipment | Autonomous equipment Sensor failure Compatibility issues
 | New Technology Integration & Training | Training for new equipment Reliability of new systems Integration challenges

## Slide 50: Construction Study (HAZOP) Guide Words Library
        Return to contents page
Category | Guide Word | Prompt Cues
Vehicles and Equipment | Vehicle Operation & Safety | Access routes and turning radii Blind spot and reversing aids Bus transport and limitations Emergency response Flashing beacons and flags Fuel storage and refuelling Inspection checklists Load securing and transport safety Maintenance and defect reporting Operator competency and licensing Parking zones and separation from pedestrian areas Speed limits on site Vehicle hygiene and cleaning Vehicle idling policies Vehicle standards (4x4, diesel) Washdown protocols
 | Equipment Compliance & Control | Equipment inspections Equipment parking near sensitive areas Exclusion zones and spotter requirements Fire suppression systems Forklift/pedestrian separation Interaction with overhead loads Lighting and visibility aids Mobile plant standards Overhead/underground utility strikes during equipment operation Pre-start checks and logbooks Stability and ground conditions Station assets (cranes, pressure vessels) Test and tag requirements
Category | Guide Word | Prompt Cues
Waste and Hazardous Materials | Hazardous Waste Handling & Disposal | Chemical mixing or disposal Lead, asbestos, PCBs, SF6, mercury Oil-contaminated rags/soil Spill containment for paints, solvents, and fuels Temporary hazardous waste bunding and signage Storage duration limits for hazardous waste Temporary storage for demolition waste Waste handling PPE requirements - gloves, masks, suits, eye protection Waste tracking and disposal documentation - manifests, certificates, registers
 | General Waste & Recycling | General waste and food scraps Scrap steel and oil Sewage and spoil Recycling and concrete slurry Waste minimisation strategies Waste segregation protocols onsite - colour-coded bins, signage, training
 | Waste Contractor & Compliance Coordination | Licensed waste contractor coordination - approvals, scheduling, compliance Waste storage area inspections and maintenance - integrity, access, pest control
 | Environmental & Community Impact | Community impact considerations - odour, visual impact, transport routes Waste-related emergency response plans - spills, exposure, fire Waste-related environmental monitoring - odour, leachate, runoff
 | Decontamination & Site Hygiene | Decontamination procedures for tools and PPE

## Slide 51: Construction Study (HAZOP) Guide Words Library
        Return to contents page
Category | Guide Word | Guide Word
Workforce & Supervision | Fatigue & Mental Health Management | Access to rest areas and quiet zones Break scheduling and adequacy Environmental fatigue factors Extended working hours Fatigue management Fatigue management training for supervisors Fatigue risk assessments for high-risk tasks Fatigue-related incident reporting and tracking Long travel times Mental health considerations Mental health support and resources Remote or travelling worker fatigue risks Roster design and shift rotation planning Sleep deprivation and shift rotations Stress due to schedule pressure Workload balancing across teams
 | Worker Welfare & Support | Accommodation arrangements AoD awareness Cultural awareness and inclusion Emergency contact records - up-to-date and secure Heat and cold stress management Multi-lingual communication needs Number onsite and shift patterns Onboarding and induction tracking Transport arrangements Visitor supervision requirements Welfare facilities - shaded rest areas, hydration, cooling/heating Workforce feedback mechanisms
Category | Guide Word | Prompt Cues
Workforce & Supervision (continued) | Training & Competency Development | Behavioural safety training - hazard awareness, stop work authority Daily pre-start briefings Emergency response training Inexperienced or incompetent workers Language and literacy support in training delivery PPE compliance verification Site-specific induction content Specialist task training (e.g. confined space) Training and competency verification Training for new equipment or procedures Training for subcontractors and short-term workers Training for supervisors and team leads - leadership, conflict resolution, WHS responsibilities Training matrix and tracking of expiries Verification of qualifications
 | Supervision & Behavioural Oversight | Behavioural hazards (horseplay, non-compliance) Escalation protocols - for behavioural or safety concerns Existing injuries and medical needs Rostering and overlap planning - shift transitions Site meetings and toolbox talks Supervision structure and responsibilities
 | Organisational Change & Communication | Scope changes, workforce turnover (Change Management) Language barriers, unclear instructions (Communication Risks) Leadership influence, behavioural compliance (Safety Culture) Bullying, harassment, isolation, workload stress, interpersonal conflict (Psychosocial Hazards)

## Slide 52: Construction Study (HAZOP) Guide Words Library
        Return to contents page
Category | Guide Word | Prompt Cues
Workforce & Supervision (continued) | Organisational Change & Communication | Scope changes, workforce turnover (Change Management) Language barriers, unclear instructions (Communication Risks) Leadership influence, behavioural compliance (Safety Culture) Bullying, harassment, isolation, workload stress, interpersonal conflict (Psychosocial Hazards)